Circutor CVM-C11

Modbus RTU Register Map

Product code M58541  |  CVM-C11-ITF-IN-485-ICT2

## Protocol basics

Mode: Modbus RTU. Read functions: 0x03 and 0x04 (integer registers). Write functions: 0x05 (single coil), 0x10 (multiple registers).

Every measurement value is a 32-bit integer spanning 2 consecutive registers. All addresses are hexadecimal. Maximum 20 variables (40 registers) per frame. Apply the scale in the Unit column to obtain engineering units.

Addressing note: these are protocol addresses (base 0). If your master uses PLC-style 3xxxx / 4xxxx addressing, add the offset and +1 yourself.

## Instantaneous / Max / Min measurements (Table 1)

| Parameter | Inst (hex) | Max (hex) | Min (hex) | Unit / scale |
| --- | --- | --- | --- | --- |
| Voltage L1 | 00-01 | 106-107 | 164-165 | V x10 |
| Current L1 | 02-03 | 108-109 | 166-167 | mA |
| Active power L1 | 04-05 | 10A-10B | 168-169 | W |
| Inductive reactive power L1 | 06-07 | 10C-10D | 16A-16B | var |
| Capacitive reactive power L1 | 08-09 | 10E-10F | 16C-16D | var |
| Apparent power L1 | 0A-0B | 110-111 | 16E-16F | VA |
| Power factor L1 | 0C-0D | 112-113 | 170-171 | x100 |
| Cos φ L1 | 0E-0F | 114-115 | 172-173 | x100 |
| Voltage L2 | 10-11 | 116-117 | 174-175 | V x10 |
| Current L2 | 12-13 | 118-119 | 176-177 | mA |
| Active power L2 | 14-15 | 11A-11B | 178-179 | W |
| Inductive reactive power L2 | 16-17 | 11C-11D | 17A-17B | var |
| Capacitive reactive power L2 | 18-19 | 11E-11F | 17C-17D | var |
| Apparent power L2 | 1A-1B | 120-121 | 17E-17F | VA |
| Power factor L2 | 1C-1D | 122-123 | 180-181 | x100 |
| Cos φ L2 | 1E-1F | 124-125 | 182-183 | x100 |
| Voltage L3 | 20-21 | 126-127 | 184-185 | V x10 |
| Current L3 | 22-23 | 128-129 | 186-187 | mA |
| Active power L3 | 24-25 | 12A-12B | 188-189 | W |
| Inductive reactive power L3 | 26-27 | 12C-12D | 18A-18B | var |
| Capacitive reactive power L3 | 28-29 | 12E-12F | 18C-18D | var |
| Apparent power L3 | 2A-2B | 130-131 | 18E-18F | VA |
| Power factor L3 | 2C-2D | 132-133 | 190-191 | x100 |
| Cos φ L3 | 2E-2F | 134-135 | 192-193 | x100 |
| Active power III (3-phase) | 30-31 | 136-137 | 194-195 | W |
| Inductive reactive power III | 32-33 | 138-139 | 196-197 | var |
| Capacitive reactive power III | 34-35 | 13A-13B | 198-199 | var |
| Apparent power III | 36-37 | 13C-13D | 19A-19B | VA |
| Power factor III | 38-39 | 13E-13F | 19C-19D | x100 |
| Cos φ III | 3A-3B | 140-141 | 19E-19F | x100 |
| Frequency (L1) | 3C-3D | 142-143 | 1A0-1A1 | Hz x100 |
| Voltage L1-L2 | 3E-3F | 144-145 | 1A2-1A3 | V x10 |
| Voltage L2-L3 | 40-41 | 146-147 | 1A4-1A5 | V x10 |
| Voltage L3-L1 | 42-43 | 148-149 | 1A6-1A7 | V x10 |
| Neutral current | 44-45 | 14A-14B | 1A8-1A9 | mA |
| %THD voltage L1 | 46-47 | 14C-14D | 1AA-1AB | % x10 |
| %THD voltage L2 | 48-49 | 14E-14F | 1AC-1AD | % x10 |
| %THD voltage L3 | 4A-4B | 150-151 | 1AE-1AF | % x10 |
| %THD current L1 | 4C-4D | 152-153 | 1B0-1B1 | % x10 |
| %THD current L2 | 4E-4F | 154-155 | 1B2-1B3 | % x10 |
| %THD current L3 | 50-51 | 156-157 | 1B4-1B5 | % x10 |
| Max demand, active power III | 52-53 | 158-159 | n/a | W |
| Max demand, apparent power III | 54-55 | 15A-15B | n/a | VA |
| Max demand, current AVG | 56-57 | 15C-15D | n/a | mA |
| Max demand, current L1 | 58-59 | 15E-15F | n/a | mA |
| Max demand, current L2 | 5A-5B | 160-161 | n/a | mA |
| Max demand, current L3 | 5C-5D | 162-163 | n/a | mA |
| Max demand, ind. reactive power III | 200-201 | 204-205 | n/a | kvarL |
| Max demand, cap. reactive power III | 202-203 | 206-207 | n/a | kvarC |

## Energy and tariff registers (Table 2)

| Parameter | T1 | T2 | T3 | Total | Unit |
| --- | --- | --- | --- | --- | --- |
| Active energy consumed (kW range) | 5E-5F | 88-89 | B2-B3 | DC-DD | kWh |
| Active energy consumed (W range) | 60-61 | 8A-8B | B4-B5 | DE-DF | Wh |
| Ind. reactive consumed (kvarh) | 62-63 | 8C-8D | B6-B7 | E0-E1 | kvarh |
| Ind. reactive consumed (varh) | 64-65 | 8E-8F | B8-B9 | E2-E3 | varh |
| Cap. reactive consumed (kvarh) | 66-67 | 90-91 | BA-BB | E4-E5 | kvarh |
| Cap. reactive consumed (varh) | 68-69 | 92-93 | BC-BD | E6-E7 | varh |
| Apparent consumed (kVAh) | 6A-6B | 94-95 | BE-BF | E8-E9 | kVAh |
| Apparent consumed (VAh) | 6C-6D | 96-97 | C0-C1 | EA-EB | VAh |
| CO2 emissions consumed | 6E-6F | 98-99 | C2-C3 | EC-ED | x10 |
| Cost consumed | 70-71 | 9A-9B | C4-C5 | EE-EF | x10 |
| Active energy generated (kW range) | 72-73 | 9C-9D | C6-C7 | F0-F1 | kWh |
| Active energy generated (W range) | 74-75 | 9E-9F | C8-C9 | F2-F3 | Wh |
| Ind. reactive generated (kvarh) | 76-77 | A0-A1 | CA-CB | F4-F5 | kvarh |
| Ind. reactive generated (varh) | 78-79 | A2-A3 | CC-CD | F6-F7 | varh |
| Cap. reactive generated (kvarh) | 7A-7B | A4-A5 | CE-CF | F8-F9 | kvarh |
| Cap. reactive generated (varh) | 7C-7D | A6-A7 | D0-D1 | FA-FB | varh |
| Apparent generated (kVAh) | 7E-7F | A8-A9 | D2-D3 | FC-FD | kVAh |
| Apparent generated (VAh) | 80-81 | AA-AB | D4-D5 | FE-EF | VAh |
| CO2 emissions generated | 82-83 | AC-AD | D6-D7 | 100-101 | x10 |
| Cost generated | 84-85 | AE-AF | D8-D9 | 102-103 | x10 |
| Hours per tariff | 86-87 | B0-B1 | DA-DB | 104-105 | seconds |

## Harmonics (Tables 3 and 4)

Voltage harmonics. Fundamental at A28-A29 (L1), A48-A49 (L2), A68-A69 (L3), in V x10. Orders 2 through 31 follow as single registers immediately after each fundamental: L1 A2A (2nd) through A47 (31st); L2 block starts at A4A; L3 block starts at A6A. All harmonic orders in % x10.

Current harmonics. Fundamental at A88-A89 (L1), AA8-AA9 (L2), AC8-AC9 (L3), in mA. Orders 2 through 31 follow as single registers: L1 A8A (2nd) through AA7 (31st); L2 block starts at AAA; L3 block starts at ACA. All harmonic orders in % x10.

## Write / reset commands

| Action (function 0x05, write FF00) | Address (hex) |
| --- | --- |
| Clear energies | 834 |
| Clear max/min | 838 |
| Reset max demand | 839 |
| Clear hour counters (all tariffs) | 83D |
| Clear max-demand peak | 83F |
| Clear energies + max demand + max/min | 848 |
| Power status / quadrant (read, function 0x04) | 7D1 |

Source: Circutor CVM-C11 instruction manual, document M361B01, Section 7/8 (Modbus Commands). Cross-check against the current manual at docs.circutor.com before commissioning, as Circutor may revise addresses across firmware versions.