Schneider EasyLogic PM2100 series

Modbus Register Map

PM2110 / PM2120 / PM2130  (METSEPM21xx)  |  User manual ref. NHA2779002-12

## Protocol basics

Mode: Modbus RTU over RS-485. Default: address 1, 19200 baud, even parity. Up to 32 devices per bus.

Data types. FLOAT32 = IEEE-754 32-bit float across 2 registers (big-endian, high word first). INT64 = 4 registers. 4Q_FP_PF = Schneider four-quadrant float power-factor encoding (value −2 to +2, decode per the register-list References tab). DATETIME = 4-register Schneider date/time.

Addressing. Numbers below are 1-based register numbers (as published by Schneider). On the wire, protocol/PDU address = register number − 1 (e.g. register 3000 Current A is sent as 0x0BB7). Many masters expect the −1 offset; some add it automatically. Read with function 0x03.

Model note. PM2110 has pulse output only (no RS-485). PM2120/PM2130 have RS-485. Harmonics beyond THD and some advanced items are PM2130 only.

## Real-time metering (1-second, FLOAT32)

| Register | Regs | Data type | Unit | Description |
| --- | --- | --- | --- | --- |
| 3000 | 2 | FLOAT32 | A | Current A |
| 3002 | 2 | FLOAT32 | A | Current B |
| 3004 | 2 | FLOAT32 | A | Current C |
| 3006 | 2 | FLOAT32 | A | Current N (neutral) |
| 3010 | 2 | FLOAT32 | A | Current Average |
| 3012 | 2 | FLOAT32 | % | Current Unbalance A |
| 3018 | 2 | FLOAT32 | % | Current Unbalance Worst |
| 3020 | 2 | FLOAT32 | V | Voltage A-B |
| 3022 | 2 | FLOAT32 | V | Voltage B-C |
| 3024 | 2 | FLOAT32 | V | Voltage C-A |
| 3026 | 2 | FLOAT32 | V | Voltage L-L Average |
| 3028 | 2 | FLOAT32 | V | Voltage A-N |
| 3030 | 2 | FLOAT32 | V | Voltage B-N |
| 3032 | 2 | FLOAT32 | V | Voltage C-N |
| 3036 | 2 | FLOAT32 | V | Voltage L-N Average |
| 3044 | 2 | FLOAT32 | % | Voltage Unbalance L-L Worst |
| 3052 | 2 | FLOAT32 | % | Voltage Unbalance L-N Worst |
| 3054 | 2 | FLOAT32 | kW | Active Power A |
| 3056 | 2 | FLOAT32 | kW | Active Power B |
| 3058 | 2 | FLOAT32 | kW | Active Power C |
| 3060 | 2 | FLOAT32 | kW | Active Power Total |
| 3062 | 2 | FLOAT32 | kVAR | Reactive Power A |
| 3064 | 2 | FLOAT32 | kVAR | Reactive Power B |
| 3066 | 2 | FLOAT32 | kVAR | Reactive Power C |
| 3068 | 2 | FLOAT32 | kVAR | Reactive Power Total |
| 3070 | 2 | FLOAT32 | kVA | Apparent Power A |
| 3072 | 2 | FLOAT32 | kVA | Apparent Power B |
| 3074 | 2 | FLOAT32 | kVA | Apparent Power C |
| 3076 | 2 | FLOAT32 | kVA | Apparent Power Total |
| 3078 | 2 | 4Q_FP_PF | --- | Power Factor A |
| 3080 | 2 | 4Q_FP_PF | --- | Power Factor B |
| 3082 | 2 | 4Q_FP_PF | --- | Power Factor C |
| 3084 | 2 | 4Q_FP_PF | --- | Power Factor Total |
| 3086 | 2 | 4Q_FP_PF | --- | Displacement PF A |
| 3092 | 2 | 4Q_FP_PF | --- | Displacement PF Total |
| 3110 | 2 | FLOAT32 | Hz | Frequency |

## Energy, floating point (FLOAT32, kWh / kVARh / kVAh)

| Register | Regs | Data type | Unit | Description |
| --- | --- | --- | --- | --- |
| 2700 | 2 | FLOAT32 | kWh | Active Energy Delivered (into load) |
| 2702 | 2 | FLOAT32 | kWh | Active Energy Received (out of load) |
| 2704 | 2 | FLOAT32 | kWh | Active Energy Delivered + Received |
| 2706 | 2 | FLOAT32 | kWh | Active Energy Delivered - Received |
| 2708 | 2 | FLOAT32 | kVARh | Reactive Energy Delivered |
| 2710 | 2 | FLOAT32 | kVARh | Reactive Energy Received |
| 2712 | 2 | FLOAT32 | kVARh | Reactive Energy Delivered + Received |
| 2714 | 2 | FLOAT32 | kVARh | Reactive Energy Delivered - Received |
| 2716 | 2 | FLOAT32 | kVAh | Apparent Energy Delivered |
| 2718 | 2 | FLOAT32 | kVAh | Apparent Energy Received |
| 2720 | 2 | FLOAT32 | kVAh | Apparent Energy Delivered + Received |
| 2722 | 2 | FLOAT32 | kVAh | Apparent Energy Delivered - Received |
| 2732 | 2 | FLOAT32 | kVARh | Reactive Energy in Quadrant I |
| 2734 | 2 | FLOAT32 | kVARh | Reactive Energy in Quadrant II |
| 2738 | 2 | FLOAT32 | kVARh | Reactive Energy in Quadrant III |
| 2740 | 2 | FLOAT32 | kVARh | Reactive Energy in Quadrant IV |

## Energy, integer accumulators (INT64, Wh / VARh / VAh)

| Register | Regs | Data type | Unit | Description |
| --- | --- | --- | --- | --- |
| 3204 | 4 | INT64 | Wh | Active Energy Delivered (into load) |
| 3208 | 4 | INT64 | Wh | Active Energy Received (out of load) |
| 3212 | 4 | INT64 | Wh | Active Energy Delivered + Received |
| 3216 | 4 | INT64 | Wh | Active Energy Delivered - Received |
| 3220 | 4 | INT64 | VARh | Reactive Energy Delivered |
| 3224 | 4 | INT64 | VARh | Reactive Energy Received |
| 3236 | 4 | INT64 | VAh | Apparent Energy Delivered |
| 3240 | 4 | INT64 | VAh | Apparent Energy Received |
| 3200 | 4 | DATETIME | --- | Accumulated Energy Reset Date/Time |

## Demand (FLOAT32)

| Register | Regs | Data type | Unit | Description |
| --- | --- | --- | --- | --- |
| 3764 | 2 | FLOAT32 | kW | Active Power: Last Demand |
| 3766 | 2 | FLOAT32 | kW | Active Power: Present Demand |
| 3768 | 2 | FLOAT32 | kW | Active Power: Predicted Demand |
| 3770 | 2 | FLOAT32 | kW | Active Power: Peak Demand |
| 3772 | 4 | DATETIME | --- | Active Power: Peak Demand Date/Time |
| 3780 | 2 | FLOAT32 | kVAR | Reactive Power: Last Demand |
| 3786 | 2 | FLOAT32 | kVAR | Reactive Power: Peak Demand |
| 3796 | 2 | FLOAT32 | kVA | Apparent Power: Last Demand |
| 3802 | 2 | FLOAT32 | kVA | Apparent Power: Peak Demand |
| 3876 | 2 | FLOAT32 | A | Current: Last Demand (avg) |
| 3882 | 2 | FLOAT32 | A | Current: Peak Demand (avg) |

## Total harmonic distortion (FLOAT32, %)

| Register | Regs | Data type | Unit | Description |
| --- | --- | --- | --- | --- |
| 21300 | 2 | FLOAT32 | % | THD Current A |
| 21302 | 2 | FLOAT32 | % | THD Current B |
| 21304 | 2 | FLOAT32 | % | THD Current C |
| 21322 | 2 | FLOAT32 | % | THD Voltage A-B |
| 21324 | 2 | FLOAT32 | % | THD Voltage B-C |
| 21326 | 2 | FLOAT32 | % | THD Voltage C-A |
| 21330 | 2 | FLOAT32 | % | THD Voltage A-N |
| 21332 | 2 | FLOAT32 | % | THD Voltage B-N |
| 21334 | 2 | FLOAT32 | % | THD Voltage C-N |

Individual harmonic magnitudes (H1–H31, PM2130) begin at register 21712 for Voltage A-B, then 22100 for Voltage B-C, and continue in per-input blocks; each harmonic is FLOAT32 (2 registers) spaced 6 registers apart. See the full register list for the complete harmonic block.

## Key setup registers (write via command interface)

| Register | Regs | Data type | Unit | Description |
| --- | --- | --- | --- | --- |
| 2014 | 1 | INT16U | --- | Number of Phases |
| 2016 | 1 | INT16U | --- | Power System Configuration |
| 2017 | 1 | INT16U | Hz | Nominal Frequency |
| 2018 | 2 | FLOAT32 | V | Nominal Voltage |
| 2020 | 2 | FLOAT32 | A | Nominal Current |
| 2026 | 2 | FLOAT32 | V | VT Primary |
| 2028 | 1 | INT16U | V | VT Secondary |
| 2030 | 1 | INT16U | A | CT Primary |
| 2031 | 1 | INT16U | A | CT Secondary |
| 2036 | 1 | INT16U | --- | VT Connection Type |

Important: the PM2100 is NOT a simple write-anywhere map. CT/VT/system changes go through the Protected Command Interface (registers 5000–5127). Acquire the command semaphore by reading register 5001, then write the Basic Meter Setup command (2000) with the full parameter block plus the semaphore, and confirm via the Command Result registers 5125–5127 (result in 5126 must be 0). Do not write setup registers directly.

Source: Schneider Electric “EasyLogic PM2100 / PM2200 / EM6400NG Register List” (Public EM6400_PM2xxx PMC Register List). This map is shared across those families. The user manual NHA2779002-12 itself contains no register table; it directs you to this register list. Download the current version from se.com (search “PM2100 PM2200 Register List”) and verify against your firmware before commissioning.